## Introduction
APPENDIX 7 - WMS Cost Analyses for the 2011 Region M Water Plan
Cost Estimation Methodology for the 2011 Region M Water Plan Introduction In accordance with the instructions provided by the Texas Water Development Board in "Exhibit C - Guidelines for Regional Water Plan Development"(Appendix 10) individual, per-unit cost estimates were generated for the following water management strategies (WMSs) available in Region M: A. Acquisition of Rio Grande Water Rights Through Purchase B. Acquisition of Rio Grande Water Rights Through Urbanization C. Acquisition of Rio Grande Water Rights Through Contract D. Non-Potable Water Re-Use E. Potable Water Re-Use F. Advanced Water Conservation G. Seawater Desalination H. Brackish Groundwater Desalination I. Additional Groundwater J. Brownsville Weir and Reservoir K. Resaca Restoration L. Laredo Low Water Weir M. Banco Morales Reservoir N. Proposed Elevated Storage Tank and Infrastructure Improvements for City of Elsa O. On-Farm Conservation P. Conveyance System Conservation This document explains the origin and development of the per-unit cost estimates for Water Management Strategies (WMS)

## Water Rights Purchase
Water Rights Purchase
Table AWR-1. Reported and inflated construction costs of a 10 MGD surface water treatment facility.
Item | Description | US$2007
1 | Raw water intake screens/gates | 5928109.6408
2 | Raw water reservoir | 8892171.2123
3 | High service pump station | 13338263.5695
4 | Raw water pump station | 8151162.5705
5 | Flocculation/sedimentation basins | 32604623.2777
6 | Membraen filtration equipment | 31122605.9941
7 | Filter building | 5335300.027
8 | Chemical storage/feed system | 6224521.1988
9 | Administrative/lab/control building | 4149680.7992
10 | Chemical building | 2519450.9855
11 | Clearwell tank | 12597241.4256
12 | Recycle pump station | 1778428.8416
13 | Backwash waste/sludge lagoon | 4979614.2586
14 | Plant piping & valving | 19518322.3595
15 | Plant electrical | 27876958.1683
16 | Site grading & seeding | 1482030.7857
17 | Site paving | 2667650.0135
18 | Fencing | 1107077.5235
| Construction cost subtotal | 190273199.1498
Table AWR-2. Other capital outlay costs for a new 10 MGD surface water treatment facility.
Item | Description | US$2007
1 | Delivery infrastructure ($219,525/mile @ 1 mile) | 2964048.0694
2 | Engineering/Other (35%) | 66595614.9767
3 | Land and easements (5%) | 9513659.2824
4 | Environmental (1%) | 1902729.1561
5 | Purchased water cost (Purchase @ $2,300/acre foot) | 347845100
| Other Capital Outlay Costs Subtotal | 428821151.4845
Table AWR-3. Estimated debt service costs of acquisition of Rio Grande surface rights and new 10 MGD surface water treatment facility, 2007.
Item | Description | Value | Unit | Interest During Construction (IDC) Calculator
1 | Construction costs | 190273199.1498 | US$2007
2 | Other Capital Outlay Costs | 428821151.4845 | US$2007 |  | Loan Information
3 | Total initial costs (i.e., loan principle) | 619094350.6343 | US$2007 |  | Annual Interest Rate |  |  | 0.06
4 | Annual Interest Rate | 0.06 | Number |  | Monthly Interest Rate |  |  | 0.005
5 | Monthly Interest Rate | 0.005 | Number |  | Years of Loan/Lifetime |  |  | 20
6 | Years of Loan/Lifetime | 20 | Years |  | Number Monthly Payments |  |  | 240
7 | Number Monthly Payments | 240 | Number |  | Principal |  |  | 619094350.6343
8 | Monthly Payments on Loan | 4435384.2092 | US$2007
9 | Annual Payments on Loan | 53224610.5107 | US$2007 |  | Monthly Payment |  |  | 4435384.2092
10 | Interest During Construction | 24708678.7798 | US$2007 |  | Annual Payment |  |  | 53224610.5107
[5 empty] | Lifetime payments |  |  | 1064492210.2147
Table AWR-4. Acquisition of Rio Grande surface water rights estimated total annual project costs, water production, and per unit production costs, 2007.
Item | Description | Value |  | Assuming: Construction period equals 1 year
| Annual Costs |  |  | Month | Payment Number | Principle payment | Interest Payment | Total Payment | Unspent Funds | Return on Investment
[6 empty] | PPt | IPt | TPt = IPt + PPt | UFt
1 | Operations and maintenance (45%) | 53224608.8195 |  | Jan | 1 | 1339912.4561 | 3095471.7532 | 4435384.2092 | 617754438.1783 | 2059181.4606
2 | Power cost (10%) | 11827689.3485 |  | Feb | 2 | 1346612.0183 | 3088772.1909 | 4435384.2092 | 617747738.616 | 2059159.1287
| Total Annual Costs | 65052298.168 |  | Mar | 3 | 1353345.0784 | 3082039.1308 | 4435384.2092 | 617741005.5559 | 2059136.6852
| Water Production |  |  | Apr | 4 | 1360111.8038 | 3075272.4054 | 4435384.2092 | 617734238.8305 | 2059114.1294
3 | Million-Gallons-Per-Day | 135.021 |  | May | 5 | 1366912.3628 | 3068471.8464 | 4435384.2092 | 617727438.2715 | 2059091.4609
4 | 1,000 gallons/year | 49282657.7984 |  | Jun | 6 | 1373746.9247 | 3061637.2846 | 4435384.2092 | 617720603.7097 | 2059068.679
5 | acre-feet/year | 151237 |  | Jul | 7 | 1380615.6593 | 3054768.55 | 4435384.2092 | 617713734.975 | 2059045.7833
| Costs per-unit |  |  | Aug | 8 | 1387518.7376 | 3047865.4717 | 4435384.2092 | 617706831.8967 | 2059022.773
6 | $/1,000 gallons | 1.32 |  | Sep | 9 | 1394456.3313 | 3040927.878 | 4435384.2092 | 617699894.3031 | 2058999.6477
7 | $/acre-foot | 430.1348 |  | Oct | 10 | 1401428.6129 | 3033955.5963 | 4435384.2092 | 617692922.0214 | 2058976.4067
|  |  |  | Nov | 11 | 1408435.756 | 3026948.4532 | 4435384.2092 | 617685914.8783 | 2058953.0496
|  |  |  | Dec | 12 | 1415477.9348 | 3019906.2745 | 4435384.2092 | 617678872.6996 | 2058929.5757
|  |  |  | Total |  | 16528573.6759 | 36696036.8348 | 53224610.5107 |  | 24708678.7798
|  |  |  | Capital Cost | [5 empty] | 631081708.6894

## Water Rights Urbanization
Water Rights Urbanization
Table AWR-1. Reported and inflated construction costs of a 10 MGD surface water treatment facility.
Item | Description | Cost
1 | Raw water intake screens/gates | 643073.8957
2 | Raw water reservoir | 964611.5759
3 | High service pump station | 1446918.0962
4 | Raw water pump station | 884227.8882
5 | Flocculation/sedimentation basins | 3536908.6235
6 | Membraen filtration equipment | 3376141.2481
7 | Filter building | 578766.6526
8 | Chemical storage/feed system | 675228.2496 | Interest During Construction (IDC) Calculator
9 | Administrative/lab/control building | 450152.1664
10 | Chemical building | 273306.8817 |  | Loan Information
11 | Clearwell tank | 1366532.9438 |  | Annual Interest Rate |  |  | 0.06
12 | Recycle pump station | 192921.7293 |  | Monthly Interest Rate |  |  | 0.005
13 | Backwash waste/sludge lagoon | 540182.3068 |  | Years of Loan/Lifetime |  |  | 20
14 | Plant piping & valving | 2117323.1195 |  | Number Monthly Payments |  |  | 240
15 | Plant electrical | 3024057.4443 |  | Principal |  |  | 55100168.3671
16 | Site grading & seeding | 160768.8401
17 | Site paving | 289383.3263 |  | Monthly Payment |  |  | 394754.7195
18 | Fencing | 120094.3807 |  | Annual Payment |  |  | 4737056.6335
| Construction cost subtotal | 20640599.369 |  | Lifetime payments |  |  | 94741132.6694
Table AWR-2. Other capital outlay costs for a new 10 MGD surface water treatment facility. |  |  | Assuming: Construction period equals 1 year
Item | Description | US$2007 | Month | Payment Number | Principle payment | Interest Payment | Total Payment | Unspent Funds | Return on Investment
1 | Delivery infrastructure ($219,525/mile @ 1 mile) | 321536.2155 |  |  | PPt | IPt | TPt = IPt + PPt | UFt
2 | Engineering/Other (35%) | 7224208.7539 | Jan | 1 | 119253.8776 | 275500.8418 | 394754.7195 | 54980914.4895 | 183269.715
3 | Land and easements (5%) | 1032029.822 | Feb | 2 | 119850.147 | 274904.5724 | 394754.7195 | 54980914.4895 | 183267.7274
4 | Environmental (1%) | 206405.6715 | Mar | 3 | 120449.3977 | 274305.3217 | 394754.7195 | 54980914.4895 | 183265.7299
5 | Contracted water cost (Urbanization @ $1,565/acre foot) | 25675390 | Apr | 4 | 121051.6447 | 273703.0747 | 394754.7195 | 54980914.4895 | 183263.7224
| Other Capital Outlay Costs Subtotal | 34459570.4628 | May | 5 | 121656.903 | 273097.8165 | 394754.7195 | 54980914.4895 | 183261.7049
|  |  | Jun | 6 | 122265.1875 | 272489.532 | 394754.7195 | 54980914.4895 | 183259.6773
Table AWR-3. Estimated debt service costs of acquisition of Rio Grande surface rights and new 10 MGD surface water treatment facility, 2007. |  |  | Jul | 7 | 122876.5134 | 271878.206 | 394754.7195 | 54980914.4895 | 183257.6395
Item | Description | Value | Aug | 8 | 123490.896 | 271263.8235 | 394754.7195 | 54980914.4895 | 183255.5916
1 | Construction costs | 20640597.9043 | Sep | 9 | 124108.3505 | 270646.369 | 394754.7195 | 54980914.4895 | 183253.5334
2 | Other Capital Outlay Costs | 34459570.4628 | Oct | 10 | 124728.8922 | 270025.8272 | 394754.7195 | 54980914.4895 | 183251.4649
3 | Total initial costs (i.e., loan principle) | 55100168.3671 | Nov | 11 | 125352.5367 | 269402.1828 | 394754.7195 | 54980914.4895 | 183249.3861
4 | Annual Interest Rate | 0.06 | Dec | 12 | 125979.2994 | 268775.4201 | 394754.7195 | 54980914.4895 | 183247.2969
5 | Monthly Interest Rate | 0.005
6 | Years of Loan/Lifetime | 20 | Total |  |  | 3265992.9879 | 4737056.6335 |  | 2199103.1892
7 | Number Monthly Payments | 240
8 | Monthly Payments on Loan | 394754.7195 | Capital Cost | [5 empty] | 56167058.1658
9 | Annual Payments on Loan | 4737056.6335
10 | Interest During Construction | 2199103.1892
Table AWR-4. Acquisition of Rio Grande surface water rights estimated total annual project costs, water production, and per unit production costs, 2007.
Item | Description | Value
Annual Costs
1 | Operations and maintenance (45%) | 5773738.7828
2 | Power cost (10%) | 1283052.9001
| Total Annual Costs | 7056791.6829
Water Production
3 | Million-Gallons-Per-Day | 14.6469
4 | 1,000 gallons/year | 5346120.8821
5 | acre-feet/year | 16406
Costs per-unit
6 | $/1,000 gallons | 1.32
7 | $/acre-foot | 430.1348

## Water Rights Contract
Acquisition of Water Rights through Contract
Table AWR-1. Reported and inflated construction costs of a 10 MGD surface water treatment facility.
Item | Description | US$2007
1 | Raw water intake screens/gates | 183091.4401
2 | Raw water reservoir | 274637.3687
3 | High service pump station | 411956.2616
4 | Raw water pump station | 251751.0951
5 | Flocculation/sedimentation basins | 1007003.5463
6 | Membraen filtration equipment | 961230.999
7 | Filter building | 164782.3378
8 | Chemical storage/feed system | 192246.1998
9 | Administrative/lab/control building | 128164.1332
10 | Chemical building | 77813.9976 | Interest During Construction (IDC) Calculator
11 | Clearwell tank | 389069.5709
12 | Recycle pump station | 54927.3069 |  | Loan Information
13 | Backwash waste/sludge lagoon | 153796.8764 |  | Annual Interest Rate |  |  | 0.06
14 | Plant piping & valving | 602829.2266 |  | Monthly Interest Rate |  |  | 0.005
15 | Plant electrical | 860988.1947 |  | Years of Loan/Lifetime |  |  | 20
16 | Site grading & seeding | 45772.9643 |  | Number Monthly Payments |  |  | 240
17 | Site paving | 82391.1689 |  | Principal |  |  | 15954945.2393
18 | Fencing | 34192.4206
| Construction cost subtotal | 5876645.1087 |  | Monthly Payment |  |  | 114306.1831
|  |  |  | Annual Payment |  |  | 1371674.1967
Table AWR-2. Other capital outlay costs for a new 10 MGD surface water treatment facility. |  |  |  | Lifetime payments |  |  | 27433483.9339
Item | Description
1 | Delivery infrastructure ($219,525/mile @ 1 mile) | 91545.5116 | Assuming: Construction period equals 1 year
2 | Engineering/Other (35%) | 6862451.3517 | Month | Payment Number | Principle payment | Interest Payment | Total Payment | Unspent Funds | Return on Investment
3 | Land and easements (5%) | 980350.1931 |  |  | PPt | IPt | TPt = IPt + PPt | UFt
4 | Environmental (1%) | 196069.7604 | Jan | 1 | 34531.4569 | 79774.7262 | 114306.1831 | 15920413.7825 | 53068.0459
5 | Contracted water cost (Contract @ $1,000/acre foot) | 1947883.314 | Feb | 2 | 34704.1141 | 79602.0689 | 114306.1831 | 15920241.1252 | 53067.4704
| Other Capital Outlay Costs Subtotal | 10078300.1307 | Mar | 3 | 34877.6347 | 79428.5483 | 114306.1831 | 15920067.6046 | 53066.892
|  |  | Apr | 4 | 35052.0229 | 79254.1602 | 114306.1831 | 15919893.2164 | 53066.3107
Table AWR-3. Estimated debt service costs of acquisition of Rio Grande surface rights and new 10 MGD surface water treatment facility, 2007. |  |  | May | 5 | 35227.283 | 79078.9001 | 114306.1831 | 15919717.9563 | 53065.7265
Item | Description | Unit | Jun | 6 | 35403.4194 | 78902.7636 | 114306.1831 | 15919541.8199 | 53065.1394
1 | Construction costs | 5876645.1087 | Jul | 7 | 35580.4365 | 78725.7465 | 114306.1831 | 15919364.8028 | 53064.5493
2 | Other Capital Outlay Costs | 10078300.1307 | Aug | 8 | 35758.3387 | 78547.8444 | 114306.1831 | 15919186.9006 | 53063.9563
3 | Total initial costs (i.e., loan principle) | 15954945.2393 | Sep | 9 | 35937.1304 | 78369.0527 | 114306.1831 | 15919008.1089 | 53063.3604
4 | Annual Interest Rate | 0.06 | Oct | 10 | 36116.816 | 78189.367 | 114306.1831 | 15918828.4233 | 53062.7614
5 | Monthly Interest Rate | 0.005 | Nov | 11 | 36297.4001 | 78008.7829 | 114306.1831 | 15918647.8392 | 53062.1595
6 | Years of Loan/Lifetime | 20 | Dec | 12 | 36478.8871 | 77827.2959 | 114306.1831 | 15918466.3522 | 53061.5545
7 | Number Monthly Payments | 240
8 | Monthly Payments on Loan | 114306.1831 | Total |  |  | 945709.2568 | 1371674.1967 |  | 636777.9264
9 | Annual Payments on Loan | 1371674.1967
10 | Interest During Construction | 636777.9264 | Capital Cost | [5 empty] | 16263876.5697
Table AWR-4. Acquisition of Rio Grande surface water rights estimated total annual project costs, water production, and per unit production costs, 2007.
Item | Description
Annual Costs
1 | Operations and maintenance (45%) | 1643857.9699
2 | Power cost (10%) | 365301.7248
| Total Annual Costs | 2009159.6947
Water Production
3 | Million-Gallons-Per-Day | 4.1702
4 | 1,000 gallons/year | 1522109.6331
5 | acre-feet/year | 4671
Costs per-unit
6 | $/1,000 gallons | 1.32
7 | $/acre-foot | 430.1348

## Non-Potable Reuse
Non-potable water reuse
Table NPWR-1. Non-potable reuse projected initial costs, 2007.
Item | Description | US$2007
Construction
1 | Treatment system | 113651234.3144
2 | Transmission system (assumes 1 mile) | 7271971.8255
| Construction Cost Subtotal | 120923206.1399
Other Capital Outlays
3 | Engineering/Other (35%) | 42323130.4304
4 | Land and easements (5%) | 6046152.0255 | Interest During Construction (IDC) Calculator
5 | Environmental (1%) | 1209223.78
| Other Capital Outlay Costs Subtotal | 49578506.2359 |  | Loan Information
|  |  |  | Annual Interest Rate |  |  | 0.06
Table NPWR-2. Non-potable reuse debt service costs, 2007. |  |  |  | Monthly Interest Rate |  |  | 0.005
Item | Description | Value |  | Years of Loan/Lifetime |  |  | 20
1 | Construction costs | 120923206.1399 |  | Number Monthly Payments |  |  | 240
2 | Other Capital Outlay Costs | 49578506.2359 |  | Principal |  |  | 170501712.3758
3 | Total initial costs (i.e., loan principle) | 170501712.3758
4 | Annual Interest Rate | 0.06 |  | Monthly Payment |  |  | 1221527.2227
5 | Monthly Interest Rate | 0.005 |  | Annual Payment |  |  | 14658326.6724
6 | Years of Loan/Lifetime | 20 |  | Lifetime payments |  |  | 293166533.4474
7 | Number Monthly Payments | 240
8 | Monthly Payments on Loan | 1221527.2227 | Assuming: Construction period equals 1 year
9 | Annual Payments on Loan | 14658326.6724 | Month | Payment Number | Principle payment | Interest Payment | Total Payment | Unspent Funds | Return on Investment
10 | Interest During Construction | 6804894.986 |  |  | PPt | IPt | TPt = IPt + PPt | UFt
|  |  | Jan | 1 | 369018.6608 | 852508.5619 | 1221527.2227 | 170132693.715 | 567108.9791
Table NPWR-3. Non-Potable reuse total annual project costs, water production, and per unit production costs, 2007. |  |  | Feb | 2 | 370863.7541 | 850663.4686 | 1221527.2227 | 170130848.6217 | 567102.8287
Item | Description | Value | Mar | 3 | 372718.0729 | 848809.1498 | 1221527.2227 | 170128994.3029 | 567096.6477
| Annual Costs |  | Apr | 4 | 374581.6633 | 846945.5594 | 1221527.2227 | 170127130.7126 | 567090.4357
|  |  | May | 5 | 376454.5716 | 845072.6511 | 1221527.2227 | 170125257.8043 | 567084.1927
2 | O&M | 1669639.113 | Jun | 6 | 378336.8444 | 843190.3783 | 1221527.2227 | 170123375.5314 | 567077.9184
3 | Treatment | 5308540.0951 | Jul | 7 | 380228.5287 | 841298.694 | 1221527.2227 | 170121483.8472 | 567071.6128
| Total Annual Costs | 6978179.2081 | Aug | 8 | 382129.6713 | 839397.5514 | 1221527.2227 | 170119582.7045 | 567065.2757
| Water Production |  | Sep | 9 | 384040.3197 | 837486.903 | 1221527.2227 | 170117672.0562 | 567058.9069
4 | Million-Gallons-Per-Day | 41.4072 | Oct | 10 | 385960.5213 | 835566.7014 | 1221527.2227 | 170115751.8546 | 567052.5062
5 | 1,000 gallons/year | 15113640.96 | Nov | 11 | 387890.3239 | 833636.8988 | 1221527.2227 | 170113822.052 | 567046.0735
6 | acre-feet/year | 46382 | Dec | 12 | 389829.7755 | 831697.4472 | 1221527.2227 | 170111882.6004 | 567039.6087
Costs per-unit
6 | $/1,000 gallons | 0.46171 | Total |  | 4552052.7073 | 10106273.9651 | 14658326.6724 |  | 6804894.986
7 | $/acre-foot | 150.4502
|  |  | Capital Cost | [5 empty] | 173803091.3549

## Potable Water Reuse
Potable Water Reuse
Table PWR-1. Potable reuse projected initial costs, 2007.
Item | Description | US$2007 |  | Interest During Construction (IDC) Calculator
Construction
1 | Treatment system | 5056324.3417 |  |  | Loan Information
2 | Transmission system (assumes 1 mile) | 175598.4745 |  |  | Annual Interest Rate |  |  | 0.06
| Construction Cost Subtotal | 5231922.8162 |  |  | Monthly Interest Rate |  |  | 0.005
| Other Capital Outlays |  |  |  | Years of Loan/Lifetime |  |  | 20
3 | Engineering/Other (35%) | 1831172.7857 |  |  | Number Monthly Payments |  |  | 240
4 | Land and easements (5%) | 261596.3408 |  |  | Principal |  |  | 7377010.8909
5 | Environmental (1%) | 52318.9482
| Other Capital Outlay Costs Subtotal | 2145088.0747 |  |  | Monthly Payment |  |  | 52851.1972
[5 empty] | Annual Payment |  |  | 634214.3665
Table PWR-2. Potable reuse debt service costs, 2007. |  |  |  |  | Lifetime payments |  |  | 12684287.3303
Item | Description | Value | Unit
1 | Construction costs | 5231922.8162 |  | Assuming: Construction period equals 1 year
2 | Other Capital Outlay Costs | 2145088.0747 |  | Month | Payment Number | Principle payment | Interest Payment | Total Payment | Unspent Funds | Return on Investment
3 | Total initial costs (i.e., loan principle) | 7377010.8909 |  |  |  | PPt | IPt | TPt = IPt + PPt | UFt
4 | Annual Interest Rate | 0.06 |  | Jan | 1 | 15966.1428 | 36885.0545 | 52851.1972 | 7361044.7481 | 24536.8158
5 | Monthly Interest Rate | 0.005 |  | Feb | 2 | 16045.9735 | 36805.2237 | 52851.1972 | 7360964.9174 | 24536.5497
6 | Years of Loan/Lifetime | 20 |  | Mar | 3 | 16126.2033 | 36724.9939 | 52851.1972 | 7360884.6875 | 24536.2823
7 | Number Monthly Payments | 240 |  | Apr | 4 | 16206.8344 | 36644.3629 | 52851.1972 | 7360804.0565 | 24536.0135
8 | Monthly Payments on Loan | 52851.1972 |  | May | 5 | 16287.8685 | 36563.3287 | 52851.1972 | 7360723.0224 | 24535.7434
9 | Annual Payments on Loan | 634214.3665 |  | Jun | 6 | 16369.3079 | 36481.8893 | 52851.1972 | 7360641.583 | 24535.4719
10 | Interest During Construction | 294423.9311 |  | Jul | 7 | 16451.1544 | 36400.0428 | 52851.1972 | 7360559.7365 | 24535.1991
|  |  |  | Aug | 8 | 16533.4102 | 36317.787 | 52851.1972 | 7360477.4807 | 24534.9249
Table PWR-3. Potable water reuse total annual project costs, water production, and per unit production costs, 2007. |  |  |  | Sep | 9 | 16616.0772 | 36235.12 | 52851.1972 | 7360394.8137 | 24534.6494
Item | Description | Value |  | Oct | 10 | 16699.1576 | 36152.0396 | 52851.1972 | 7360311.7333 | 24534.3724
| Annual Costs |  |  | Nov | 11 | 16782.6534 | 36068.5438 | 52851.1972 | 7360228.2375 | 24534.0941
1 | O&M | 40317.2741 |  | Dec | 12 | 16866.5667 | 35984.6305 | 52851.1972 | 7360144.3242 | 24533.8144
2 | Treatment | 128186.9024
| Total Annual Costs | 168504.1765 |  | Total |  | 196951.3498 | 437263.0167 | 634214.3665 |  | 294423.9311
Water Production
3 | Million-Gallons-Per-Day | 0.99987 |  | Capital Cost | [5 empty] | 7519849.9765
4 | 1,000 gallons/year | 364953.6
5 | acre-feet/year | 1120
Costs per-unit
6 | $/1,000 gallons | 0.46171
7 | $/acre-foot | 150.4502

## Advanced Water Conservation
Advanced Water Conservation
Table AC-1. Advanced conservation projected initial costs, 2007.
Item | Description | US$2007 |  | Interest During Construction (IDC) Calculator
Initial Capital Costs
1 | School Education @ $5/student (2000 population) | 3106510.5128 |  |  | Loan Information
2 | Public Education @ $5/person (2010 population) | 12126288.3929 |  |  | Annual Interest Rate |  |  | 0.06
| Construction Cost Subtotal | 15232798.9057 |  |  | Monthly Interest Rate |  |  | 0.005
| Other Capital Outlays |  |  |  | Years of Loan/Lifetime |  |  | 20
3 | Delivery infrastructure ($219,525/mile) @ 1 mile | 380289.6632 |  |  | Number Monthly Payments |  |  | 240
4 | Engineering/Other (35%) | 5331480.0501 |  |  | Principal |  |  | 21858535.3407
5 | Land and easements (5%) | 761639.5122
6 | Environmental (1%) | 152327.2095 |  |  | Monthly Payment |  |  | 156601.3361
| Other Capital Outlay Costs Subtotal | 6625736.435 |  |  | Annual Payment |  |  | 1879216.0333
[5 empty] | Lifetime payments |  |  | 37584320.6663
Table AC-2. Advanced conservation debt service costs, 2007. |  |  |  | Assuming: Construction period equals 1 year
Item | Description | Value | Unit | Month | Payment Number | Principle payment | Interest Payment | Total Payment | Unspent Funds | Return on Investment
1 | Construction costs | 15232798.9057 |  |  |  | PPt | IPt | TPt = IPt + PPt | UFt
2 | Other capital outlays | 6625736.435 |  | Jan | 1 | 47308.6594 | 109292.6767 | 156601.3361 | 21811226.6813 | 72704.0889
3 | Total initial costs (i.e., loan principle) | 21858535.3407 |  | Feb | 2 | 47545.2027 | 109056.1334 | 156601.3361 | 21810990.138 | 72703.3005
4 | Annual Interest Rate | 0.06 |  | Mar | 3 | 47782.9287 | 108818.4074 | 156601.3361 | 21810752.412 | 72702.508
5 | Monthly Interest Rate | 0.005 |  | Apr | 4 | 48021.8434 | 108579.4927 | 156601.3361 | 21810513.4974 | 72701.7117
6 | Years of Loan/Lifetime | 20 |  | May | 5 | 48261.9526 | 108339.3835 | 156601.3361 | 21810273.3882 | 72700.9113
7 | Number Monthly Payments | 240 |  | Jun | 6 | 48503.2623 | 108098.0738 | 156601.3361 | 21810032.0784 | 72700.1069
8 | Monthly Payments on Loan | 156601.3361 |  | Jul | 7 | 48745.7787 | 107855.5575 | 156601.3361 | 21809789.5621 | 72699.2985
9 | Annual Payments on Loan | 1879216.0333 |  | Aug | 8 | 48989.5075 | 107611.8286 | 156601.3361 | 21809545.8332 | 72698.4861
10 | Interest During Construction | 872396.1506 |  | Sep | 9 | 49234.4551 | 107366.881 | 156601.3361 | 21809300.8856 | 72697.6696
|  |  |  | Oct | 10 | 49480.6274 | 107120.7088 | 156601.3361 | 21809054.7134 | 72696.849
|  |  |  | Nov | 11 | 49728.0305 | 106873.3056 | 156601.3361 | 21808807.3102 | 72696.0244
Table AC-3. Advanced conservation total annual project costs, water production, and per unit production costs, 2007. |  |  |  | Dec | 12 | 49976.6706 | 106624.6655 | 156601.3361 | 21808558.6701 | 72695.1956
Item | Description | Value
| Annual Costs |  |  | Total |  | 583578.9189 | 1597571.2597 | 1879216.0333 |  | 872396.1506
| Total Annual Costs |  |  | Capital Cost | [5 empty] | 22583710.4498
Water Production
1 | Million-Gallons-Per-Day | 29.2764
2 | 1,000 gallons/year | 10685875.3566
3 | acre-feet/year | 32793
NO ANNUAL COSTS
Costs per-unit
4 | $/1,000 gallons
5 | $/acre-foot

## Seawater Desalination
Seawater Desalination
Construction Costs
Item | Description
Desalination
1 | Site Development | 6828393.1218
2 | Seawater Intake System | 10960282.2911
3 | Pretreatment System | 20672096.7709
4 | Primary Treatment System | 12513569.7967
5 | Post Treatment System | 425752.2578
6 | Solids Handling System | 1795255.3539
7 | Yard Piping | 1277256.7735
8 | Support Facilities | 9307417.4145
9 | Electrical and Instrumentation | 7095870.9641
10 | Subtotal | 70875894.7444 | Interest During Construction (IDC) Calculator
11 | Effective Contingency | 7087588.3932
12 | Total Desalination Plant | 77963483.1375 |  | Loan Information
Brine Disposal System |  |  |  | Annual Interest Rate |  |  | 0.06
13 | Brine Transfer Pump Station | 2703188.9387 |  | Monthly Interest Rate |  |  | 0.005
14 | Brine Disposal Main (Open-cut Land Installation) | 37755439.9067 |  | Years of Loan/Lifetime |  |  | 20
15 | Brine Disposal Main (Ocean Installation | 1365110.414 |  | Number Monthly Payments |  |  | 240
16 | Brine Disposal Main (Bench head) | 4054783.408 |  | Principal |  |  | 182409000
17 | Diffuser Array | 1351594.4693
18 | Easement Acquisition | 1567849.5844 |  | Monthly Payment |  |  | 1306834.7295
19 | Subtotal | 48797966.7213 |  | Annual Payment |  |  | 15682016.7535
20 | Contingency | 4879796.6721 |  | Lifetime payments |  |  | 313640335.0703
21 | Total Brine Disposal | 53677763.3934
Finished Water Transmission System |  |  | Assuming: Construction period equals 1 year
22 | Finished Water Transfer & HS Pumps | 2459901.9342 | Month | Payment Number | Principle payment | Interest Payment | Total Payment | Unspent Funds | Return on Investment
23 | Finished Water Transmission System | 6163270.7802 |  |  | PPt | IPt | TPt = IPt + PPt | UFt
24 | 2.0 MG Ground Storage Tank | 3481437.0341 | Jan | 1 | 394789.7295 | 912045 | 1306834.7295 | 182014210.2705 | 606714.0342
25 | Land and Right of Way | 810956.6816 | Feb | 2 | 396763.6781 | 910071.0514 | 1306834.7295 | 182012236.3219 | 606707.4544
26 | Subtotal | 12915566.4302 | Mar | 3 | 398747.4965 | 908087.233 | 1306834.7295 | 182010252.5035 | 606700.8417
27 | Effective Contingency | 1291556.643 | Apr | 4 | 400741.234 | 906093.4955 | 1306834.7295 | 182008258.766 | 606694.1959
28 | Total Finished Water | 14207123.0732 | May | 5 | 402744.9401 | 904089.7893 | 1306834.7295 | 182006255.0599 | 606687.5169
29 | TOTAL Construction Cost | 145848369.6042 | Jun | 6 | 404758.6649 | 902076.0646 | 1306834.7295 | 182004241.3351 | 606680.8045
|  |  | Jul | 7 | 406782.4582 | 900052.2713 | 1306834.7295 | 182002217.5418 | 606674.0585
Other Capital Outlays |  |  | Aug | 8 | 408816.3705 | 898018.359 | 1306834.7295 | 182000183.6295 | 606667.2788
1 | Design Determination Studies | 8020361.5811 | Sep | 9 | 410860.4523 | 895974.2771 | 1306834.7295 | 181998139.5477 | 606660.4652
2 | Design and Specifications | 16043426.3511 | Oct | 10 | 412914.7546 | 893919.9749 | 1306834.7295 | 181996085.2454 | 606653.6175
3 | Environmental Review and Permitting | 2916740.8649 | Nov | 11 | 414979.3284 | 891855.4011 | 1306834.7295 | 181994020.6716 | 606646.7356
4 | Construction Support Services | 7293203.7566 | Dec | 12 | 417054.225 | 889780.5045 | 1306834.7295 | 181991945.775 | 606639.8193
5 | Startup Support Services | 2286897.8421
6 | Total Project Implementation | 36560630.3958 | Total |  | 4869953.3319 | 10812063.4216 | 15682016.7535 |  | 7280126.8222
Item | Description | Unit | Capital Cost | [5 empty] | 185940936.5994
1 | Construction costs | 145848369.6042
2 | Other Capital Outlay Costs | 36560630.3958
3 | Total initial costs (i.e., loan principle) | 182409000
4 | Annual Interest Rate | 0.06
5 | Monthly Interest Rate | 0.005
6 | Years of Loan/Lifetime | 20
7 | Number Monthly Payments | 240
8 | Monthly Payments on Loan | 1306834.7295
9 | Annual Payments on Loan | 15682016.7535
10 | Interest During Construction | 7280126.8222
Item | Description | Value
Annual Costs
1 | Operations and maintenance | 19814910
2 | Power cost | 9605980
| Total Annual Costs | 29420890
Water Production
3 | Million-Gallons-Per-Day | 25
4 | 1,000 gallons/year | 9125000
5 | acre-feet/year | 28003.5599
Costs per-unit
6 | $/1,000 gallons | 3.2242
7 | $/acre-foot | 1050.6125

## Brackish Desalination
Brackish groundwater desalination
The cost estimate for the brackish groundwater desalination WMS is largely derived from cost data published in the Guidance Manual for Brackish Groundwater Desalination in Texas (2008). The Guidance Manual cited the experience and knowledge gained during development of the North Cameron Regional Water Project (North Cameron). This project, a brackish groundwater desalination facility with a capacity of 2.25 million gallons per day, provides the construction cost data used in the development the per unit cost estimation used in the Plan for the WMS, brackish groundwater desalination (Table BWRO-1. The construction period for North Cameron ended in 2007, so no additional manipulation (i.e., inflating or discounting) of the cost data was done.
Table BWRO-1. Brackish groundwater desalination construction cost data from North Cameron Regional Water Project, 2007.
Item | Description | US$2007
1 | Reverse osmosis building, concentrate lines, off-site | 18852689.881
2 | Reverse osmosis system | 50749117.7381
3 | Production well | 11688920.9524
4 | Ground storage tank (2 MG) | 28672602.381
5 | Site fencing | 978221.3095
6 | High service pump system and chlorination building | 8250763.6905 |  | Interest During Construction (IDC) Calculator
7 | Secondary containment (pipes, valves, pumps, and installation) | 9052779.4048
8 | PVC piping (valves, accessories, pumps and wet well) | 11592495.8333 |  |  | Loan Information
9 | Electrical supervisory control and data acquisition | 31524441.4286 |  |  | Annual Interest Rate |  |  | 0.06
10 | Chlorination | 1842860.7143 |  |  | Monthly Interest Rate |  |  | 0.005
11 | Paving, grading, and flatwork (sidewalks and driveway) | 2310020.3571 |  |  | Years of Loan/Lifetime |  |  | 20
12 | Ductile iron header | 227619.0476 |  |  | Number Monthly Payments |  |  | 240
13 | Culvert | 113809.5238 |  |  | Principal |  |  | 258592337.9762
14 | Irrigation line | 104960.8333
15 | Transformer pad and conduit from service to pad | 248389.2857 |  |  | Monthly Payment |  |  | 1852635.8241
16 | Temporary power hookup | 52636.9048 |  |  | Annual Payment |  |  | 22231629.8893
| Construction cost subtotal | 176262329.2857 |  |  | Lifetime payments |  |  | 444632597.7855
Assuming: Construction period equals 1 year
| In addition to construction costs, water projects, such as North Cameron, incur a variety of pre-construction costs and/or planning costs. These costs, which include water delivery infrastructure, engineering, land and easement purchases, are categorized as “Other capital outlays” per Exhibit B (Table BWRO-2). Note the “purchased water cost” for brackish groundwater desalination is not available (N/A). For groundwater, this cost is presumed to be zero. |  |  | Month | Payment Number | Principle payment | Interest Payment | Total Payment | Unspent Funds | Return on Investment
[6 empty] | PPt | IPt | TPt = IPt + PPt | UFt
Table BWRO-2. Brackish groundwater desalination other capital outlay cost data from North Cameron Regional Water Project and estimations, 2007 |  |  |  | Jan | 1 | 559674.1342 | 1292961.6899 | 1852635.8241 | 258032663.842 | 860108.8795
Item | Description | US$2007 |  | Feb | 2 | 562472.5049 | 1290163.3192 | 1852635.8241 | 258029865.4713 | 860099.5516
| Data from Guidance Manual |  |  | Mar | 3 | 565284.8674 | 1287350.9567 | 1852635.8241 | 258027053.1088 | 860090.177
1 | Test wells | 1138095.2381 |  | Apr | 4 | 568111.2918 | 1284524.5323 | 1852635.8241 | 258024226.6844 | 860080.7556
2 | Test well evaluation | 853571.4286 |  | May | 5 | 570951.8482 | 1281683.9759 | 1852635.8241 | 258021386.128 | 860071.2871
3 | Laboratory testing | 1824736.5476 |  | Jun | 6 | 573806.6075 | 1278829.2166 | 1852635.8241 | 258018531.3687 | 860061.7712
| Estimations (with assumptions) | 0 |  | Jul | 7 | 576675.6405 | 1275960.1836 | 1852635.8241 | 258015662.3357 | 860052.2078
4 | Delivery infrastructure ($219,525/mile) @ 1 mile | 6246037.381 |  | Aug | 8 | 579559.0187 | 1273076.8054 | 1852635.8241 | 258012778.9575 | 860042.5965
5 | Engineering/Other (35%) | 61691818.0952 |  | Sep | 9 | 582456.8138 | 1270179.0103 | 1852635.8241 | 258009881.1624 | 860032.9372
6 | Land and easements (5%) | 8813125 |  | Oct | 10 | 585369.0979 | 1267266.7262 | 1852635.8241 | 258006968.8783 | 860023.2296
7 | Environmental (1%) | 1762625 |  | Nov | 11 | 588295.9433 | 1264339.8808 | 1852635.8241 | 258004042.0328 | 860013.4734
8 | Purchased water cost | N/A |  | Dec | 12 | 591237.4231 | 1261398.401 | 1852635.8241 | 258001100.5531 | 860003.6685
| Other Capital Outlay Costs Subtotal | 82330008.6905
|  |  |  | Total |  | 6903895.1912 | 15327734.698 | 22231629.8893 |  | 10320680.5351
The construction and other capital outlay costs were compiled and a single debt service cost was estimated to cover these initial project costs (Table BWRO-3). The lifetime of the loan and the project are both assumed to be for 20 years. Interest for the loan is assumed to be 6%.
|  |  |  | Capital Cost | [5 empty] | 263599392.1392
Table BWRO-3. Brackish groundwater desalination estimated debt service costs, 2007.
Item | Description | Value | Unit
1 | Construction costs | 176262329.2857
2 | Other Capital Outlay Costs | 82330008.6905
3 | Total initial costs (i.e., loan principle) | 258592337.9762
4 | Annual Interest Rate | 0.06
5 | Monthly Interest Rate | 0.005
6 | Years of Loan/Lifetime | 20
7 | Number Monthly Payments | 240
8 | Monthly Payments on Loan | 1852635.8241
9 | Annual Payments on Loan | 22231629.8893
10 | Interest During Construction | 10320680.5351
Table BWRO-4: Brackish groundwater desalination estimated total annual project costs, water production, and per unit production costs, 2007.
Item | Description | Value
Annual Costs
2 | Operations and maintenance (30%) | 16673721.1905
3 | Power cost (30%) | 16673721.1905
| Total Annual Costs | 33347442.381
Water Production
4 | Million-Gallons-Per-Day | 64.0179
5 | 1,000 gallons/year | 23366517.8571
6 | acre-feet/year | 71700
Costs per-unit
6 | $/1,000 gallons | 1.4271
7 | $/acre-foot | 465.0968

## Additional Groundwater
Additional Groundwater
Table #GW Additional groundwater projected initial costs, 2007.
Item | Description | US$2007
Construction
1 | Wellfield | 3265444.415
2 | Water Treatment Facility (32 MGD) | 15849753.7321
| Construction Cost Subtotal | 19115198.1472
Other Capital Outlays
3 | Delivery infrastructure ($219,525/mile) @ 1 mile | 219525
4 | Engineering/Other (35%) | 6690319.3515
5 | Land and easements (5%) | 955759.9074
6 | Environmental (1%) | 191151.9815
| Other Capital Outlay Costs Subtotal | 7837231.2403
Interest During Construction (IDC) Calculator
Table #GW Additional groundwater debt service costs, 2007.
Item | Description |  |  | Loan Information
1 | Construction costs | 44047049.9548 |  | Annual Interest Rate |  |  | 0.06
2 | Other capital outlays | 18059290.4814 |  | Monthly Interest Rate |  |  | 0.005
3 | Total initial costs (i.e., loan principle) | 62106340.4362 |  | Years of Loan/Lifetime |  |  | 20
4 | Annual Interest Rate | 0.06 |  | Number Monthly Payments |  |  | 240
5 | Monthly Interest Rate | 0.005 |  | Principal |  |  | 62106340.4362
6 | Years of Loan/Lifetime | 20
7 | Number Monthly Payments | 240 |  | Monthly Payment |  |  | 444949.1122
8 | Monthly Payments on Loan | 444949.1122 |  | Annual Payment |  |  | 5339389.346
9 | Annual Payments on Loan | 5339389.346 |  | Lifetime payments |  |  | 106787786.9206
10 | Interest During Construction | 2478726.5696
Assuming: Construction period equals 1 year
|  |  | Month | Payment Number | Principle payment | Interest Payment | Total Payment | Unspent Funds | Return on Investment
Item | Description |  |  |  | PPt | IPt | TPt = IPt + PPt | UFt
| Annual Costs |  | Jan | 1 | 134417.41 | 310531.7022 | 444949.1122 | 61971923.0262 | 206573.0768
|  |  | Feb | 2 | 135089.497 | 309859.6151 | 444949.1122 | 61971250.9392 | 206570.8365
1 | O&M Wellfield | 1618672.2631 | Mar | 3 | 135764.9445 | 309184.1676 | 444949.1122 | 61970575.4917 | 206568.585
2 | O&M Water Treatment Facility | 3652129.2935 | Apr | 4 | 136443.7692 | 308505.3429 | 444949.1122 | 61969896.667 | 206566.3222
| Total Annual Costs | 5270801.5566 | May | 5 | 137125.9881 | 307823.1241 | 444949.1122 | 61969214.4481 | 206564.0482
| Water Production |  | Jun | 6 | 137811.618 | 307137.4941 | 444949.1122 | 61968528.8182 | 206561.7627
3 | Million-Gallons-Per-Day | 21.8901 | Jul | 7 | 138500.6761 | 306448.436 | 444949.1122 | 61967839.7601 | 206559.4659
4 | 1,000 gallons/year | 7989877.0286 | Aug | 8 | 139193.1795 | 305755.9327 | 444949.1122 | 61967147.2567 | 206557.1575
5 | acre-feet/year | 24520 | Sep | 9 | 139889.1454 | 305059.9668 | 444949.1122 | 61966451.2908 | 206554.8376
| Costs per-unit |  | Oct | 10 | 140588.5911 | 304360.521 | 444949.1122 | 61965751.8451 | 206552.5062
6 | $/1,000 gallons | 0.65968 | Nov | 11 | 141291.5341 | 303657.5781 | 444949.1122 | 61965048.9021 | 206550.163
7 | $/acre-foot | 214.9593 | Dec | 12 | 141997.9918 | 302951.1204 | 444949.1122 | 61964342.4445 | 206547.8081
|  |  | Total |  | 1658114.3449 | 3681275.0011 | 5339389.346 |  | 2478726.5696
|  |  | Capital Cost | [5 empty] | 63308888.8677

## Brownsville Weir and Reservoir
Table BWR-1. Brownsville Weir & Reservoir projected initial costs, 2007.
Item | Description | US$2007
Construction
1 | Weir & Reservoir construction | 34026480
2 | Water Treatment Facility (35 MGD) | 32654444
3 | Treated Water Storage | 1632722
| Construction Cost Subtotal | 68313646
Other Capital Outlays
4 | Delivery infrastructure ($219,525/mile) @ 1 mile | 219525
5 | Engineering/Other (35%) | 23909776
6 | Land and easements (5%) | 3415682
7 | Environmental (1%) | 683136
| Other Capital Outlay Costs Subtotal | 28228119
Table BWR-2. Brownsville Weir & Reservoir debt service costs, 2007.
Item | Description | Value
1 | Construction costs | 68313646 | Interest During Construction (IDC) Calculator
2 | Other Capital Outlay Costs | 28228119
3 | Total initial costs (i.e., loan principle) | 96541765 |  | Loan Information
4 | Annual Interest Rate | 0.06 |  | Annual Interest Rate |  |  | 0.06
5 | Monthly Interest Rate | 0.005 |  | Monthly Interest Rate |  |  | 0.005
6 | Years of Loan/Lifetime | 20 |  | Years of Loan/Lifetime |  |  | 20
7 | Number Monthly Payments | 240 |  | Number Monthly Payments |  |  | 240
8 | Monthly Payments on Loan | 691655.1889 |  | Principal |  |  | 96541765
9 | Annual Payments on Loan | 8299862.2664
10 | Interest During Construction | 3853079.0303 |  | Monthly Payment |  |  | 691655.1889
|  |  |  | Annual Payment |  |  | 8299862.2664
Table BWR-3. Brownsville Weir & Reservoir total annual project costs, water production, and per unit production costs, 2007. Water production approximated at 20,643 acre-feet per year (18.43 MGD). |  |  |  | Lifetime payments |  |  | 165997245.3271
Item | Description | Value
| Annual Costs |  | Assuming: Construction period equals 1 year
|  |  | Month | Payment Number | Principle payment | Interest Payment | Total Payment | Unspent Funds | Return on Investment
2 | O&M Water treatment facility | 3265444 |  |  | PPt | IPt | TPt = IPt + PPt | UFt
3 | O&M Weir and Reservoir | 510397 | Jan | 1 | 208946.3639 | 482708.825 | 691655.1889 | 96332818.6361 | 321109.3955
| Total Annual Costs | 3775841 | Feb | 2 | 209991.0957 | 481664.0932 | 691655.1889 | 96331773.9043 | 321105.913
| Water Production |  | Mar | 3 | 211041.0512 | 480614.1377 | 691655.1889 | 96330723.9488 | 321102.4132
4 | Million-Gallons-Per-Day | 18.43 | Apr | 4 | 212096.2564 | 479558.9324 | 691655.1889 | 96329668.7436 | 321098.8958
5 | 1,000 gallons/year | 6726950 | May | 5 | 213156.7377 | 478498.4512 | 691655.1889 | 96328608.2623 | 321095.3609
6 | acre-feet/year | 20644.2244 | Jun | 6 | 214222.5214 | 477432.6675 | 691655.1889 | 96327542.4786 | 321091.8083
| Costs per-unit |  | Jul | 7 | 215293.634 | 476361.5549 | 691655.1889 | 96326471.366 | 321088.2379
6 | $/1,000 gallons | 1.7816 | Aug | 8 | 216370.1022 | 475285.0867 | 691655.1889 | 96325394.8978 | 321084.6497
7 | $/acre-foot | 182.9006 | Sep | 9 | 217451.9527 | 474203.2362 | 691655.1889 | 96324313.0473 | 321081.0435
|  |  | Oct | 10 | 218539.2124 | 473115.9764 | 691655.1889 | 96323225.7876 | 321077.4193
|  |  | Nov | 11 | 219631.9085 | 472023.2804 | 691655.1889 | 96322133.0915 | 321073.777
|  |  | Dec | 12 | 220730.068 | 470925.1208 | 691655.1889 | 96321034.932 | 321070.1164
|  |  | Total |  | 2577470.904 | 5722391.3623 | 8299862.2664 |  | 3853079.0303
|  |  | Capital Cost | [5 empty] | 98411077.332

## Resaca Restoration
Table RR-1. Resaca Restoration
Item | Description | US$2007
Construction
1 | Resaca construction | 28056745.2
| Construction Cost Subtotal | 28056745.2
Other Capital Outlays
4 | Delivery infrastructure @ 1 mile | 229555.188
5 | Engineering/Other (35%) | 19512190.98
6 | Land and easements (5%) | 2754662.256
7 | Environmental (1%) | 459110.376
| Other Capital Outlay Costs Subtotal | 22955518.8
Table RR-2. Resaca Restoration debt service costs, 2007.
Item | Description | Value | Unit | Interest During Construction (IDC) Calculator
1 | Construction costs | 28056745.2 | US$2007
2 | Other Capital Outlay Costs | 22955518.8 | US$2007 |  | Loan Information
3 | Total initial costs (i.e., loan principle) | 51012264 | US$2007 |  | Annual Interest Rate |  |  | 0.06
4 | Annual Interest Rate | 0.06 | Number |  | Monthly Interest Rate |  |  | 0.005
5 | Monthly Interest Rate | 0.005 | Number |  | Years of Loan/Lifetime |  |  | 20
6 | Years of Loan/Lifetime | 20 | Years |  | Number Monthly Payments |  |  | 240
7 | Number Monthly Payments | 240 | Number |  | Principal |  |  | 51012264
8 | Monthly Payments on Loan | 365467.7029 | US$2007
9 | Annual Payments on Loan | 4385612.4351 | US$2007 |  | Monthly Payment |  |  | 365467.7029
10 | Interest During Construction | 2035950.8106 | US$2007 |  | Annual Payment |  |  | 4385612.4351
[5 empty] | Lifetime payments |  |  | 87712248.7029
Table RR-3. Resaca Restoration total annual project costs, water production, and per unit production costs, 2007. Water production approximated at 20,643 acre-feet per year (18.43 MGD).
Item | Description | Value |  | Assuming: Construction period equals 1 year
| Annual Costs |  |  | Month | Payment Number | Principle payment | Interest Payment | Total Payment | Unspent Funds | Return on Investment
[6 empty] | PPt | IPt | TPt = IPt + PPt | UFt
3 | O&M Resacas | 510397 |  | Jan | 1 | 110406.3829 | 255061.32 | 365467.7029 | 50901857.6171 | 169672.8587
| Total Annual Costs | 510397 |  | Feb | 2 | 110958.4148 | 254509.2881 | 365467.7029 | 50901305.5852 | 169671.0186
| Water Production |  |  | Mar | 3 | 111513.2069 | 253954.496 | 365467.7029 | 50900750.7931 | 169669.1693
4 | Million-Gallons-Per-Day | 0.75 |  | Apr | 4 | 112070.773 | 253396.93 | 365467.7029 | 50900193.227 | 169667.3108
5 | 1,000 gallons/year | 273750 |  | May | 5 | 112631.1268 | 252836.5761 | 365467.7029 | 50899632.8732 | 169665.4429
6 | acre-feet/year | 877 |  | Jun | 6 | 113194.2825 | 252273.4205 | 365467.7029 | 50899069.7175 | 169663.5657
| Costs per-unit |  |  | Jul | 7 | 113760.2539 | 251707.4491 | 365467.7029 | 50898503.7461 | 169661.6792
6 | $/1,000 gallons | 24.75 |  | Aug | 8 | 114329.0551 | 251138.6478 | 365467.7029 | 50897934.9449 | 169659.7831
7 | $/acre-foot | 2542 |  | Sep | 9 | 114900.7004 | 250567.0025 | 365467.7029 | 50897363.2996 | 169657.8777
|  |  |  | Oct | 10 | 115475.2039 | 249992.499 | 365467.7029 | 50896788.7961 | 169655.9627
|  |  |  | Nov | 11 | 116052.5799 | 249415.123 | 365467.7029 | 50896211.4201 | 169654.0381
|  |  |  | Dec | 12 | 116632.8428 | 248834.8601 | 365467.7029 | 50895631.1572 | 169652.1039
|  |  |  | Total |  | 1361924.823 | 3023687.6122 | 4385612.4351 |  | 2035950.8106
|  |  |  | Capital Cost | [5 empty] | 52000000.8016

## Laredo Low Water Weir
Table LLWW-1. Laredo Low Water Weir projected initial costs
Item | Description | US$2007
Construction
1 | Weir & Reservoir construction | 122463545
2 | Water Treatment Facility (35 MGD) | 31840521.7
3 | Treated Water Storage | 90623023.3
| Construction Cost Subtotal | 244927090
Other Capital Outlays
4 | Delivery infrastructure @ 1 mile | 434883.99
5 | Engineering/Other (35%) | 36965139.15
6 | Land and easements (5%) | 5218607.88
7 | Environmental (1%) | 869767.98
| Other Capital Outlay Costs Subtotal | 43488399
Table LLWW-2. Laredo Low Water Weir debt service costs, 2007.
Item | Description | Value
1 | Construction costs | 244927090 | Interest During Construction (IDC) Calculator
2 | Other Capital Outlay Costs | 43488399
3 | Total initial costs (i.e., loan principle) | 288415489 |  | Loan Information
4 | Annual Interest Rate | 0.06 |  | Annual Interest Rate |  |  | 0.06
5 | Monthly Interest Rate | 0.005 |  | Monthly Interest Rate |  |  | 0.005
6 | Years of Loan/Lifetime | 20 |  | Years of Loan/Lifetime |  |  | 20
7 | Number Monthly Payments | 240 |  | Number Monthly Payments |  |  | 240
8 | Monthly Payments on Loan | 2066298.1407 |  | Principal |  |  | 288415489
9 | Annual Payments on Loan | 24795577.6879
10 | Interest During Construction | 11510952.5156 |  | Monthly Payment |  |  | 2066298.1407
|  |  |  | Annual Payment |  |  | 24795577.6879
Table LLWW-3. Laredo Low Water Weir total annual project costs, water production, and per unit production costs, 2007. Water production approximated at 20,643 acre-feet per year (18.43 MGD). |  |  |  | Lifetime payments |  |  | 495911553.7578
Item | Description | Value
| Annual Costs |  | Assuming: Construction period equals 1 year
1 | O&M Weir and Reservoir | 205000 | Month | Payment Number | Principle payment | Interest Payment | Total Payment | Unspent Funds | Return on Investment
| Total Annual Costs | 205000 |  |  | PPt | IPt | TPt = IPt + PPt | UFt
| Costs per-unit |  | Jan | 1 | 624220.6957 | 1442077.445 | 2066298.1407 | 287791268.3043 | 959304.2277
2 | $/1,000 gallons | 13.69 | Feb | 2 | 627341.7991 | 1438956.3415 | 2066298.1407 | 287788147.2009 | 959293.824
3 | $/acre-foot | 4460 | Mar | 3 | 630478.5081 | 1435819.6325 | 2066298.1407 | 287785010.4919 | 959283.3683
|  |  | Apr | 4 | 633630.9007 | 1432667.24 | 2066298.1407 | 287781858.0993 | 959272.8603
|  |  | May | 5 | 636799.0552 | 1429499.0855 | 2066298.1407 | 287778689.9448 | 959262.2998
|  |  | Jun | 6 | 639983.0505 | 1426315.0902 | 2066298.1407 | 287775505.9495 | 959251.6865
|  |  | Jul | 7 | 643182.9657 | 1423115.175 | 2066298.1407 | 287772306.0343 | 959241.0201
|  |  | Aug | 8 | 646398.8805 | 1419899.2601 | 2066298.1407 | 287769090.1195 | 959230.3004
|  |  | Sep | 9 | 649630.8749 | 1416667.2657 | 2066298.1407 | 287765858.1251 | 959219.5271
|  |  | Oct | 10 | 652879.0293 | 1413419.1113 | 2066298.1407 | 287762609.9707 | 959208.6999
|  |  | Nov | 11 | 656143.4245 | 1410154.7162 | 2066298.1407 | 287759345.5755 | 959197.8186
|  |  | Dec | 12 | 659424.1416 | 1406873.9991 | 2066298.1407 | 287756064.8584 | 959186.8829
|  |  | Total |  | 7700113.3257 | 17095464.3622 | 24795577.6879 |  | 11510952.5156
|  |  | Capital Cost | [5 empty] | 294000000.8466

## Banco Morales Reservoir
Table BMR-1. Banco Morales Reservoir projected initial costs
Item | Description | US$2007
Construction
1 | Weir & Reservoir construction | 8981539.405
2 | Water Treatment Facility (35 MGD) | 8442647.0407
3 | Treated Water Storage | 538892.3643
| Construction Cost Subtotal | 17963078.81
Other Capital Outlays
4 | Delivery infrastructure ($219,525/mile) @ 1 mile | 73370.3219
5 | Engineering/Other (35%) | 6236477.3615
6 | Land and easements (5%) | 880443.8628
7 | Environmental (1%) | 146740.6438
| Other Capital Outlay Costs Subtotal | 7337032.19
Table BMR-2. Banco Morales Reservoir debt service costs
Item | Description | Value | Unit
1 | Construction costs | 17963078.81 | US$2007 | Interest During Construction (IDC) Calculator
2 | Other Capital Outlay Costs | 7337032.19 | US$2007
3 | Total initial costs (i.e., loan principle) | 25300111 | US$2007 |  | Loan Information
4 | Annual Interest Rate | 0.06 | Number |  | Annual Interest Rate |  |  | 0.06
5 | Monthly Interest Rate | 0.005 | Number |  | Monthly Interest Rate |  |  | 0.005
6 | Years of Loan/Lifetime | 20 | Years |  | Years of Loan/Lifetime |  |  | 20
7 | Number Monthly Payments | 240 | Number |  | Number Monthly Payments |  |  | 240
8 | Monthly Payments on Loan | 181257.853 | US$2007 |  | Principal |  |  | 25300111
9 | Annual Payments on Loan | 2175094.2364 | US$2007
10 | Interest During Construction | 1009752.8998 | US$2007 |  | Monthly Payment |  |  | 181257.853
[5 empty] | Annual Payment |  |  | 2175094.2364
Table BMR-3. Banco Morales Reservoir total annual project costs, water production, and per unit production costs |  |  |  |  | Lifetime payments |  |  | 43501884.728
Item | Description | Value
| Annual Costs |  |  | Assuming: Construction period equals 1 year
|  |  |  | Month | Payment Number | Principle payment | Interest Payment | Total Payment | Unspent Funds | Return on Investment
2 | O&M Water treatment facility | 47850 |  |  |  | PPt | IPt | TPt = IPt + PPt | UFt
3 | O&M Weir and Reservoir | 7150 |  | Jan | 1 | 54757.298 | 126500.555 | 181257.853 | 25245353.702 | 84151.179
| Total Annual Costs | 55000 |  | Feb | 2 | 55031.0845 | 126226.7685 | 181257.853 | 25245079.9155 | 84150.2664
| Water Production |  |  | Mar | 3 | 55306.2399 | 125951.6131 | 181257.853 | 25244804.7601 | 84149.3492
4 | Million-Gallons-Per-Day | 4.7065 |  | Apr | 4 | 55582.7711 | 125675.0819 | 181257.853 | 25244528.2289 | 84148.4274
5 | 1,000 gallons/year | 77554.918 |  | May | 5 | 55860.685 | 125397.168 | 181257.853 | 25244250.315 | 84147.501
6 | acre-feet/year | 238 |  | Jun | 6 | 56139.9884 | 125117.8646 | 181257.853 | 25243971.0116 | 84146.57
| Costs per-unit |  |  | Jul | 7 | 56420.6884 | 124837.1647 | 181257.853 | 25243690.3116 | 84145.6344
6 | $/1,000 gallons | 1.4101 |  | Aug | 8 | 56702.7918 | 124555.0612 | 181257.853 | 25243408.2082 | 84144.694
7 | $/acre-foot | 231.0924 |  | Sep | 9 | 56986.3058 | 124271.5473 | 181257.853 | 25243124.6942 | 84143.749
|  |  |  | Oct | 10 | 57271.2373 | 123986.6157 | 181257.853 | 25242839.7627 | 84142.7992
|  |  |  | Nov | 11 | 57557.5935 | 123700.2595 | 181257.853 | 25242553.4065 | 84141.8447
|  |  |  | Dec | 12 | 57845.3815 | 123412.4716 | 181257.853 | 25242265.6185 | 84140.8854
|  |  |  | Total |  | 675462.0653 | 1499632.1711 | 2175094.2364 |  | 1009752.8998
|  |  |  | Capital Cost | [5 empty] | 25789990.2714

## Proposed Elsa Infrastructure
Proposed Elevated Storage Tank and Infrastructure Improvements for the City of Elsa
Construction
Item | Description | US$2010
1 | 0.5 MG Elevated Storage | 950000
2 | Substandard Waterline Replacement | 101500
3 | Substandard Wastewater Line Replacement | 340000
4 | Rehad/New Lift Service Stations | 4000000
5 | Substandard Waterline Replacement | 280000
6 | Proposed Water Line | 196000 |  | Interest During Construction (IDC) Calculator
7 | Proposed Wastewater Line | 153000
| Construction Cost Subtotal | 6020500 |  |  | Loan Information
[5 empty] | Annual Interest Rate |  |  | 0.06
[5 empty] | Monthly Interest Rate |  |  | 0.005
Item | Description | US$2010 |  |  | Years of Loan/Lifetime |  |  | 20
1 | Planning | 196945 |  |  | Number Monthly Payments |  |  | 240
2 | Design | 196945 |  |  | Principal |  |  | 8718886
3 | Construction | 56270
4 | Environmental | 67524 |  |  | Monthly Payment |  |  | 62464.8073
5 | Surveying | 39389 |  |  | Annual Payment |  |  | 749577.6871
6 | Geotechnical | 33762 |  |  | Lifetime payments |  |  | 14991553.7418
7 | Testing | 28135
8 | Inspection | 56270 |  | Assuming: Construction period equals 1 year
9 | GIS Asset Management Project | 300000 |  | Month | Payment Number | Principle payment | Interest Payment | Total Payment | Unspent Funds | Return on Investment
10 | Contingency | 747906 |  |  |  | PPt | IPt | TPt = IPt + PPt | UFt
11 | Professional Engineering Fees | 975240 |  | Jan | 1 | 18870.3773 | 43594.43 | 62464.8073 | 8700015.6227 | 29000.0521
| Other Capital Outlay Subtotal | 2698386 |  | Feb | 2 | 18964.7291 | 43500.0781 | 62464.8073 | 8699921.2709 | 28999.7376
|  |  |  | Mar | 3 | 19059.5528 | 43405.2545 | 62464.8073 | 8699826.4472 | 28999.4215
|  |  |  | Apr | 4 | 19154.8506 | 43309.9567 | 62464.8073 | 8699731.1494 | 28999.1038
|  |  |  | May | 5 | 19250.6248 | 43214.1825 | 62464.8073 | 8699635.3752 | 28998.7846
Item | Description | Value | Unit | Jun | 6 | 19346.8779 | 43117.9293 | 62464.8073 | 8699539.1221 | 28998.4637
1 | Construction costs | 6020500 |  | Jul | 7 | 19443.6123 | 43021.1949 | 62464.8073 | 8699442.3877 | 28998.1413
2 | Other Capital Outlay Costs | 2698386 |  | Aug | 8 | 19540.8304 | 42923.9769 | 62464.8073 | 8699345.1696 | 28997.8172
3 | Total initial costs (i.e., loan principle) | 8718886 |  | Sep | 9 | 19638.5345 | 42826.2727 | 62464.8073 | 8699247.4655 | 28997.4916
4 | Annual Interest Rate | 0.06 |  | Oct | 10 | 19736.7272 | 42728.0801 | 62464.8073 | 8699149.2728 | 28997.1642
5 | Monthly Interest Rate | 0.005 |  | Nov | 11 | 19835.4108 | 42629.3964 | 62464.8073 | 8699050.5892 | 28996.8353
6 | Years of Loan/Lifetime | 20 |  | Dec | 12 | 19934.5879 | 42530.2194 | 62464.8073 | 8698951.4121 | 28996.5047
7 | Number Monthly Payments | 240
8 | Monthly Payments on Loan | 62464.8073 |  | Total |  |  | 516800.9714 | 749577.6871 |  | 347979.5176
9 | Annual Payments on Loan | 749577.6871
10 | Interest During Construction | 347979.5176 |  | Capital Cost | [5 empty] | 8887707.4538
Description | Value
Annual Costs
Operations and maintenance (45%) |  | 10705
Total Annual Costs |  | 10705
Water Production
Million-Gallons-Per-Day |  | 0.1
1,000 gallons/year |  | 34214
acre-feet/year |  | 105
Costs per-unit
$/1,000 gallons |  | 0.31288
$/acre-foot |  | 101.9524

## Irrigation On-Farm Conservation
Irrigation On Farm Conservation
CONSTRUCTION CAPITAL COSTS
Construction Costs |  | 241221309 | Interest During Construction (IDC) Calculator
| Construction Capital Costs Subtotal | 241221309
Loan Information
|  |  |  | Annual Interest Rate |  |  | 0.06
OTHER CAPITAL OUTLAYS |  |  |  | Monthly Interest Rate |  |  | 0.005
1 | Engineering, Legal Costs, Financing, & Contingencies (35%) | 84427458 |  | Years of Loan/Lifetime |  |  | 20
2 | Land Acquisition & Easements (5%) | 12061065 |  | Number Monthly Payments |  |  | 240
3 | Environmental & Arch. Studies & Mitigation & Permitting (1%) | 2412213 |  | Principal |  |  | 340122045
| Other Capital Outlays Subtotal | 98900736
|  |  |  | Monthly Payment |  |  | 2436739.9671
Item | Description |  |  | Annual Payment |  |  | 29240879.6053
1 | Construction costs | 241221309 |  | Lifetime payments |  |  | 584817592.1067
2 | Other capital outlays | 98900736
3 | Total initial costs (i.e., loan principle) | 340122045 | Assuming: Construction period equals 1 year
4 | Annual Interest Rate | 0.06 | Month | Payment Number | Principle payment | Interest Payment | Total Payment | Unspent Funds | Return on Investment
5 | Monthly Interest Rate | 0.005 |  |  | PPt | IPt | TPt = IPt + PPt | UFt
6 | Years of Loan/Lifetime | 20 | Jan | 1 | 736129.7421 | 1700610.225 | 2436739.9671 | 1700610.225 | 5668.7008
7 | Number Monthly Payments | 240 | Feb | 2 | 739810.3908 | 1696929.5763 | 2436739.9671 | 1696929.5763 | 5656.4319
8 | Monthly Payments on Loan | 2436739.9671 | Mar | 3 | 743509.4428 | 1693230.5243 | 2436739.9671 | 1693230.5243 | 5644.1017
9 | Annual Payments on Loan | 29240879.6053 | Apr | 4 | 747226.99 | 1689512.9771 | 2436739.9671 | 1689512.9771 | 5631.7099
10 | Interest During Construction | 67201.0175 | May | 5 | 750963.1249 | 1685776.8422 | 2436739.9671 | 1685776.8422 | 5619.2561
|  |  | Jun | 6 | 754717.9406 | 1682022.0265 | 2436739.9671 | 1682022.0265 | 5606.7401
Item | Description | Value | Jul | 7 | 758491.5303 | 1678248.4368 | 2436739.9671 | 1678248.4368 | 5594.1615
| Annual Costs |  | Aug | 8 | 762283.9879 | 1674455.9792 | 2436739.9671 | 1674455.9792 | 5581.5199
|  |  | Sep | 9 | 766095.4079 | 1670644.5593 | 2436739.9671 | 1670644.5593 | 5568.8152
| Operation and Maintenance | 39776678 | Oct | 10 | 769925.8849 | 1666814.0822 | 2436739.9671 | 1666814.0822 | 5556.0469
|  |  | Nov | 11 | 773775.5143 | 1662964.4528 | 2436739.9671 | 1662964.4528 | 5543.2148
| Total Annual Costs | 39776678 | Dec | 12 | 777644.3919 | 1659095.5752 | 2436739.9671 | 1659095.5752 | 5530.3186
| Water Production |  | Total |  | 9080574.3484 | 20160305.257 | 29240879.6053 |  | 67201.0175
4 | Million-Gallons-Per-Day | 195
5 | 1,000 gallons/year | 71290659 | Capital Cost | [5 empty] | 360215149.2395
6 | acre-feet/year | 219228
Costs per-unit
6 | $/1,000 gallons | 0.55795
7 | $/acre-foot | 181.4398

## Conveyance System
Conveyance Improvements
CONSTRUCTION CAPITAL COSTS
Construction Costs |  | 20020648 | Interest During Construction (IDC) Calculator
| Construction Capital Costs Subtotal | 20020648
Loan Information
|  |  |  | Annual Interest Rate |  |  | 0.06
OTHER CAPITAL OUTLAYS |  |  |  | Monthly Interest Rate |  |  | 0.005
1 | Engineering, Legal Costs, Financing, & Contingencies (35%) | 7007227 |  | Years of Loan/Lifetime |  |  | 20
2 | Land Acquisition & Easements (5%) | 1991932 |  | Number Monthly Payments |  |  | 240
3 | Environmental & Arch. Studies & Mitigation & Permitting (1%) | 200206 |  | Principal |  |  | 29220013
| Other Capital Outlays Subtotal | 9199365
|  |  |  | Monthly Payment |  |  | 209341.2484
Item | Description |  |  | Annual Payment |  |  | 2512094.9811
1 | Construction costs | 20020648 |  | Lifetime payments |  |  | 50241899.6216
2 | Other capital outlays | 9199365
3 | Total initial costs (i.e., loan principle) | 29220013 | Assuming: Construction period equals 1 year
4 | Annual Interest Rate | 0.06 | Month | Payment Number | Principle payment | Interest Payment | Total Payment | Unspent Funds | Return on Investment
5 | Monthly Interest Rate | 0.005 |  |  | PPt | IPt | TPt = IPt + PPt | UFt
6 | Years of Loan/Lifetime | 20 | Jan | 1 | 63241.1834 | 146100.065 | 209341.2484 | 146100.065 | 487.0002
7 | Number Monthly Payments | 240 | Feb | 2 | 63557.3893 | 145783.8591 | 209341.2484 | 145783.8591 | 485.9462
8 | Monthly Payments on Loan | 209341.2484 | Mar | 3 | 63875.1763 | 145466.0721 | 209341.2484 | 145466.0721 | 484.8869
9 | Annual Payments on Loan | 2512094.9811 | Apr | 4 | 64194.5522 | 145146.6963 | 209341.2484 | 145146.6963 | 483.8223
10 | Interest During Construction | 5773.2647 | May | 5 | 64515.5249 | 144825.7235 | 209341.2484 | 144825.7235 | 482.7524
|  |  | Jun | 6 | 64838.1026 | 144503.1459 | 209341.2484 | 144503.1459 | 481.6772
Item | Description | Value | Jul | 7 | 65162.2931 | 144178.9554 | 209341.2484 | 144178.9554 | 480.5965
| Annual Costs |  | Aug | 8 | 65488.1045 | 143853.1439 | 209341.2484 | 143853.1439 | 479.5105
|  |  | Sep | 9 | 65815.5451 | 143525.7034 | 209341.2484 | 143525.7034 | 478.419
| Operation and Maintenance | 211440.88 | Oct | 10 | 66144.6228 | 143196.6256 | 209341.2484 | 143196.6256 | 477.3221
|  |  | Nov | 11 | 66475.3459 | 142865.9025 | 209341.2484 | 142865.9025 | 476.2197
| Total Annual Costs | 211440.88 | Dec | 12 | 66807.7226 | 142533.5258 | 209341.2484 | 142533.5258 | 475.1118
| Water Production |  | Total |  | 780115.5627 | 1731979.4184 | 2512094.9811 |  | 5773.2647
4 | Million-Gallons-Per-Day | 195.3169
5 | 1,000 gallons/year | 71290659.333 | Capital Cost | [5 empty] | 30946219.1537
6 | acre-feet/year | 218783 |  |  | 141.4471
Costs per-unit
6 | $/1,000 gallons | 0.0029659
7 | $/acre-foot | 0.96644